## Sheet1
Operating Parameter (R-22) Low Range High Range (R-410) Low Range High Range
System Suction Pressure |  |  | 55 PSIG 80 PSIG | 80PSIG* | 99 PSIG | 139 PSIG*
System High Side Pressure |  |  | 180 PSIG | 295 PSIG | 295 PSIG | 488 PSIG
*Normal Conditions excluding low ambient operation
System Suction Superheat
Captube/Piston Metering |  |  | 5 Degrees F | 33 Degrees F | 5 Degrees F | 33 Degrees F
Expansion Valve Metering |  |  | 8 Degrees F** | 15 Degrees F | 8 Degrees F** | 15 Degrees F
System Subcooling 10 Seer |  |  | 5 Degrees F | 15 Degrees F | N/A | N/A
|  | 12 Seer | 10 Degrees F | 20 Degrees F | 10 Degrees F | 25 Degrees F
|  | 14 Seer |  |  | 10 Degrees F | 25 Degrees F
Evaporator Coil
Temperature Drop |  |  | 15 Degrees F | 25 Degrees F | 15 Degrees F | 25 Degrees F
Airflow/ton cooling |  |  | 350 CFM/Ton | 450 CFM/TON | 350 CFM/Ton | 450 CFM/TON
Coil Temperature |  |  | 30 Degrees F | 48 Degrees F | 30 Degrees F | 48 Degrees F
Suction Line |  |  |  | 4 Degrees F |  | 4 Degrees F
Driers |  |  |  | 3 Degrees F |  | 3 Degrees F
Indoor/Outdoor Temp Split |  |  | 15 Degrees F | 25 Degrees F | 15 Degrees F | 25 Degrees F
*Some high efficiency equipment may run a suction pressure that is designed at full load to be very high.
Verify with superheat charging charts as to whether the system's suction pressure is abnormal.
If you need additional help, contact the factory rep for for further information.
**Expansion valve settings lower than 10 degrees may cause the valve to begin to "hunt".