Steve LeMay:

In regard to the terminations illustrated, the objective is to achieve a desired minimum separation

between the inlet and outlet. As we can see, the lateral objective is 9 inches (center-to-center). This

may be achieved by using elbows to turn laterally if the holes are actually drilled closer together than

9 inches. Consider the illustrations on the bottom of this figure taken from the current Trane

TDY/TUY furnace Installer Guide. Imagine that the elbow closest to the wall is rotated 90° clockwise

and enough pipe attached to the elbow to give you a minimum of 9 inches lateral separation before

attaching another elbow to turn out away from the wall. An installation described this way would

meet the intent of the Installer Guide.

Please let me know if there are any further questions, and if we can be of any further assistance.

Sincerely,

David J. Small

David Small

After Sales Support

Trane Residential Systems